## Summary
ANSRWRF
Field Capacity and Effluent Transmission Evaluation
Max Design Flow
7.0749 | = Facility Design Flow (MGD) |  |  |  | 6 | = No. of Pumps Provided
| Operational |  |  |  | 4127.0136 | = Minimum Flow per Pump
8 | = Hours/Day |  |  | 24 | 145.9895 | = @ PSI
5 | = Days /Week |  |  | 7
10 | = Months/Year
24762.0816 | = Maximum Design Flow (gpm)
1.65 | = Inch per Week Application
40 | = Operating Hours/Week |  |  | 168
[9 empty] | Starting El. | 21
Field | GPM | Wet Acres | Avg GPD |  | Segment | GPM | Dia. | Friction | Run | Friction | Static | TDH | PSI | Field Loss | Nozzle | Total
1 | 9415.9979 | 504.4566 | 2690522.9411 |  | 1 | 24759.8929 | 24 | 10.8133 | S | 94.2675 | 34 | 128.2675 | 55.5271 | 20 | 40 | 115.5271
2 | 1951.3998 | 104.5451 | 557592.092 |  | 2 | 9415.9979 | 24 | 83.4542 | N | 175.6358 | 23 | 198.6358 | 85.9895 | 20 | 40 | 145.9895
3 | 1942.3451 | 104.06 | 555004.8023 |  | 3 | 15343.8949 | 24 | 82.4633 | W | 129.1724 | 27 | 156.1724 | 67.6071 | 20 | 40 | 127.6071
4 | 1633.1629 | 87.4958 | 466659.2235 |  | 4 | 4987.3792 | 16 | 31.829 | E | 182.0027 | 13 | 195.0027 | 84.4168 | 20 | 40 | 144.4168
5 | 1402.8164 | 75.1551 | 400840.1211 |  | 5 | 3354.2162 | 14 | 28.5662
6 | 5606.634 | 300.3722 | 1602037.0254 |  | 6 | 1402.8164 | 12 | 28.3309
7 | 2807.5367 | 150.4121 | 802224.2453 |  | 7 | 1942.3451 | 10 | 35.8958
Total | 24759.8929 | 1326.4969 | 7074880.4507 |  | 8 | 8414.1707 | 24 | 69.6883
[5 empty] | 9 | 2807.5367 | 16 | 12.671
Run | Feeding
Flow | S
1 | 1-7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
24759.8929 | 24759.8929 | 9415.9979 | 1951.3998 | 1942.3451 | 1633.1629 | 1402.8164 | 5606.634 | 2807.5367
2 | 1 | 1
9415.9979 | 9415.9979 | 9415.9979
N
3 | 2-7 | 2 | 3 | 4 | 5 | 6 | 7
15343.8949 | 15343.8949 | 1951.3998 | 1942.3451 | 1633.1629 | 1402.8164 | 5606.634 | 2807.5367
8 | 6-7 | 6 | 7
8414.1707 | 8414.1707 | 5606.634 | 2807.5367
9 | 7 | 7
2807.5367 | 2807.5367 | 2807.5367
W
7 | 3 | 3
1942.3451 | 1942.3451 | 1942.3451
E
4 | 4,2,5 | 4 | 2 | 5
4987.3792 | 4987.3792 | 1633.1629 | 1951.3998 | 1402.8164
5 | 2,5 | 2 | 5
3354.2162 | 3354.2162 | 1951.3998 | 1402.8164
6 | 5 | 5
1402.8164 | 1402.8164 | 1402.8164

## Fields
| WETTED FIELD AREAS | [24 empty] | PR. FIELD EQUIPMENT FLOW RATE PER B. WALLS: |  |  |  |  | 1000 | GPM
| Spray Field 1 | [5 empty] | FIELD 1 (G) | [10 empty] | IF HR>24 |  |  |  |  | speed at
[16 empty] | GIVEN IN/WK |  | Q ELSE |  |  |  |  | last
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX |  | .5 Q | Length to last tower | % full | area | circumference | tower | time-full cycle | time-full cycle | flow | total vol appl | total vol appl | inches appl | rate
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | Number heads | GPM | Number heads | GPM | HOUR/WK |  |  | (ft) | circle | (sq ft) | (ft) | (fpm) | (min) | (hr) | (gpm) | (gal) | (cu ft) | (in) | (in/hr)
PR | 1W-1 | 17.3034 | 753737 | 2.5 | 0.35714 | 22432.6488 | 167796.2131 | 1 | 0.14286 | 8973.0595 | 67118.4852 | 23 | 1081 | 23 | 1081 | 11.9511 |  | 540.5
| 1W-2 | 17.8869 | 779155 | 2.5 | 0.35714 | 23189.1369 | 173454.744 | 1 | 0.14286 | 9275.6548 | 69381.8976 | 25 | 1175 | 25 | 1175 | 11.3658 |  | 587.5
| 1W-3 | 14.05 | 612020 | 2.5 | 0.35714 | 18214.881 | 136247.3095 | 1 | 0.14286 | 7285.9524 | 54498.9238 | 21 | 987 | 21 | 987 | 10.6283 |  | 493.5
| 1W-4 | 13.477 | 587056 | 2.5 | 0.35714 | 17471.9048 | 130689.8476 | 1 | 0.14286 | 6988.7619 | 52275.939 | 21 | 987 | 21 | 987 | 10.1948 |  | 493.5
| 1W-5 | 13.6517 | 594668 | 2.5 | 0.35714 | 17698.4524 | 132384.4238 | 1 | 0.14286 | 7079.381 | 52953.7695 | 21 | 987 | 21 | 987 | 10.3269 |  | 493.5
| 1W-6 | 12.8087 | 557948 | 2.5 | 0.35714 | 16605.5952 | 124209.8524 | 1 | 0.14286 | 6642.2381 | 49683.941 | 21 | 987 | 21 | 987 | 9.6893 |  | 493.5
| 1W-7 | 13.8261 | 602266 | 2.5 | 0.35714 | 17924.5833 | 134075.8833 | 1 | 0.14286 | 7169.8333 | 53630.3533 | 21 | 987 | 21 | 987 | 10.4589 |  | 493.5
| 1W-8 | 13.2036 | 575148 | 2.5 | 0.35714 | 17117.5 | 128038.9 | 1 | 0.14286 | 6847 | 51215.56 | 19 | 893 | 19 | 893 | 11.0393 |  | 446.5
| 1W-9 | 9.7151 | 423189 | 2.5 | 0.35714 | 12594.9107 | 94209.9321 | 1 | 0.14286 | 5037.9643 | 37683.9729 | 16 | 752 | 16 | 752 | 9.6456 |  | 376
| 1W-10 | 12.8474 | 559634 | 2.5 | 0.35714 | 16655.7738 | 124585.1881 | 1 | 0.14286 | 6662.3095 | 49834.0752 | 20 | 940 | 20 | 940 | 10.2045 |  | 470
| 1W-11 | 12.6796 | 552324 | 2.5 | 0.35714 | 16438.2143 | 122957.8429 | 1 | 0.14286 | 6575.2857 | 49183.1371 | 20 | 940 | 20 | 940 | 10.0712 |  | 470
| 1W-12 | 15.4384 | 672497 | 2.5 | 0.35714 | 20014.7917 | 149710.6417 | 1 | 0.14286 | 8005.9167 | 59884.2567 | 24 | 1128 | 24 | 1128 | 10.2187 |  | 564
EX | SPRAY 1 | 134.0295 | 5838324 | 2.5 | 0.35714 | 173759.6429 | 1299722.1286 | 1 | 0.14286 | 69503.8571 | 519888.8514 |  | 1200 |  | 1200 | 83.3915 |  | 1200 | 1029 | 0.5 | 1663222.1486 | 3232.6961 | 9.1 | 355.2413 | 5.9207 | 1200 | 426289.5969 | 56990.5878 | 0.41118 | 0.069448
EX | SPRAY 2 | 43.685 | 1902920 | 2.5 | 0.35714 | 56634.5238 | 423626.2381 | 1 | 0.14286 | 22653.8095 | 169450.4952 |  | 1200 |  | 1200 | 27.1803 |  | 1200 | 1186 | 1 | 4418947.9276 | 7451.8515 | didn't provide | #VALUE! | #VALUE! | 1200 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
PR | SPRAY 3 | 22.4315 | 977116 | 2.5 | 0.35714 | 29080.8333 | 217524.6333 | 1 | 0.14286 | 11632.3333 | 87009.8533 |  | 1200 |  | 1200 | 13.9566 |  | 600
PR | SPRAY 4 | 55.6013 | 2421993 | 2.5 | 0.35714 | 72083.125 | 539181.775 | 1 | 0.14286 | 28833.25 | 215672.71 |  | 1200 |  | 1200 | 34.5944 |  | 1200
PR | SPRAY 5 | 25.2791 | 1101158 | 2.5 | 0.35714 | 32772.5595 | 245138.7452 | 1 | 0.14286 | 13109.0238 | 98055.4981 | Given in/wk&mo | 1200 |  | 1200 | 15.7283 |  | 600
PR | SPRAY 6 | 56.5422 | 2462977 | 2.5 | 0.35714 | 73302.8869 | 548305.594 | 1 | 0.14286 | 29321.1548 | 219322.2376 | Capacity (avg gpd) | 1200 |  | 1200 | 35.1798 |  | 1200
| TOTAL | 504.4566 |  |  |  | 653991.9643 | 4891859.8929 |  |  | 261596.7857 | 1956743.9571 | 2690522.9411 | 19044 |  |  | 19.7774 | Given Hrs/wk - GPM | 11922
| GROSS | 590 | [10 empty] | GPM Hrs |  |  | 376639.9176 |  | 0.62602
| % COVERAGE | 85.5% | [10 empty] | Given Hrs/wk |  |  | 9415.9979
| Spray Field 2 | [5 empty] | FIELD 2 (F)
GIVEN IN/WK
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY |  | GPM | Number heads | GPM | HOUR/WK
EX | SPRAY 1 | 30.9034 | 1346151 | 2.5 | 0.35714 | 40064.0179 | 299678.8536 | 1 | 0.14286 | 16025.6071 | 119871.5414 |  | 1000 |  | 1000 | 23.0732 |  | 500 | 548 | 1 | 943432.0434 | 3443.1826 | 18.21 | 189.082 | 3.1514 | 1000 | 189081.9681 | 25278.338 | 0.32153 | 0.10203
EX | SPRAY 2 | 61.3461 | 2672234 | 2.5 | 0.35714 | 79530.7738 | 594890.1881 | 1 | 0.14286 | 31812.3095 | 237956.0752 |  | 850 |  | 850 | 53.8853 |  | 850 | 841 | 1 | 2221986.9168 | 5284.1544 | 18.21 | 290.1787 | 4.8363 | 850 | 246651.9068 | 32974.8539 | 0.17808 | 0.036822
PR | SPRAY 3 | 3.7334 | 162626 | 2.5 | 0.35714 | 4840.0595 | 36203.6452 | 1 | 0.14286 | 1936.0238 | 14481.4581 | Given in/wk&mo | 850 |  | 850 | 3.2793 |  | 425
PR | SPRAY 4 | 8.5623 | 372974 | 2.5 | 0.35714 | 11100.4167 | 83031.1167 | 1 | 0.14286 | 4440.1667 | 33212.4467 | Capacity (avg gpd) | 1200 |  | 1200 | 5.3274 |  | 600
| TOTAL | 104.5451 |  |  |  | 135535.2679 | 1013803.8036 |  |  | 54214.1071 | 405521.5214 | 557592.092 | 3900 |  |  | 20.0144 | Given Hrs/wk - GPM | 2375
| GROSS | 140.9 | [10 empty] | GPM Hrs |  |  | 78055.9929 |  | 0.60897
| % COVERAGE | 74.2% | [10 empty] | Given Hrs/wk |  |  | 1951.3998
| Spray Field 3 | [5 empty] | FIELD 3 (E)
GIVEN IN/WK
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY |  | GPM | Number heads | GPM | HOUR/WK
PR | 3W-1 | 13.5166 | 588782 | 2.5 | 0.35714 | 17523.2738 | 131074.0881 | 1 | 0.14286 | 7009.3095 | 52429.6352 | 16 | 752 | 16 | 752 | 13.42 |  | 376
EX | SPRAY 1 | 83.1691 | 3622844 | 2.5 | 0.35714 | 107822.7381 | 806514.081 | 1 | 0.14286 | 43129.0952 | 322605.6324 |  | 850 |  | 850 | 73.0542 |  | 850 | 1028 | 0.75 | 2489986.5349 | 4844.3318 | 9.1 | 532.3442 | 8.8724 | 850 | 452492.5289 | 60493.6536 | 0.29154 | 0.032859
PR | SPRAY 2 | 1.7705 | 77121 | 2.5 | 0.35714 | 2295.2679 | 17168.6036 | 1 | 0.14286 | 918.1071 | 6867.4414 | Given in/wk&mo | 850 |  | 850 | 1.5551 |  | 425
PR | SPRAY 3 | 5.6039 | 244107 | 2.5 | 0.35714 | 7265.0893 | 54342.8679 | 1 | 0.14286 | 2906.0357 | 21737.1471 | Capacity (avg gpd) | 850 |  | 850 | 4.9224 |  | 425
| TOTAL | 104.06 |  |  |  | 134906.369 | 1009099.6405 |  |  | 53962.5476 | 403639.8562 | 555004.8023 | 3302 |  |  | 23.5293 | Given Hrs/wk - GPM | 2076
| GROSS | 137 | [10 empty] | GPM Hrs |  |  | 77693.8044 |  | 0.62871
| % COVERAGE | 75.96% | [10 empty] | Given Hrs/wk |  |  | 1942.3451
| Spray Field 4 | [5 empty] | FIELD 4 (D)
GIVEN IN/WK
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY |  | GPM | Number heads | GPM | HOUR/WK
PR | 4W-1 | 9.1463 | 398415 | 2.5 | 0.35714 | 11857.5893 | 88694.7679 | 1 | 0.14286 | 4743.0357 | 35477.9071 | 13 | 611 | 13 | 611 | 11.1766 |  | 305.5
| 4W-2 | 10.4086 | 453398 | 2.5 | 0.35714 | 13493.9881 | 100935.031 | 1 | 0.14286 | 5397.5952 | 40374.0124 | 16 | 752 | 16 | 752 | 10.3342 |  | 376
| 4W-3 | 12.4936 | 544221 | 2.5 | 0.35714 | 16197.0536 | 121153.9607 | 1 | 0.14286 | 6478.8214 | 48461.5843 | 18 | 846 | 18 | 846 | 11.026 |  | 423
PR | SPRAY 1 | 42.451 | 1849167 | 2.5 | 0.35714 | 55034.7321 | 411659.7964 | 1 | 0.14286 | 22013.8929 | 164663.9186 |  | 1200 |  | 1200 | 26.4125 |  | 1200
PR | SPRAY 2 | 3.34 | 145492 | 2.5 | 0.35714 | 4330.119 | 32389.2905 | 1 | 0.14286 | 1732.0476 | 12955.7162 |  | 850 |  | 850 | 2.9338 |  | 425
PR | SPRAY 3 | 5.4754 | 238508 | 2.5 | 0.35714 | 7098.4524 | 53096.4238 | 1 | 0.14286 | 2839.381 | 21238.5695 | Given in/wk&mo | 850 |  | 850 | 4.8095 |  | 425
PR | SPRAY 4 | 4.1808 | 182114 | 2.5 | 0.35714 | 5420.0595 | 40542.0452 | 1 | 0.14286 | 2168.0238 | 16216.8181 | Capacity (avg gpd) | 850 |  | 850 | 3.6723 |  | 425
| TOTAL | 87.4958 |  |  |  | 113431.994 | 848471.3155 |  |  | 45372.7976 | 339388.5262 | 466659.2235 | 5959 |  |  | 10.9627 | Given Hrs/wk - GPM | 3579.5
| GROSS | 118.9 | [10 empty] | GPM Hrs |  |  | 65326.5166 |  | 0.60069
| % COVERAGE | 73.59% | [10 empty] | Given Hrs/wk |  |  | 1633.1629
| Spray Field 5 | [5 empty] | FIELD 5 (C )
GIVEN IN/WK
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY |  | GPM | Number heads | GPM | HOUR/WK
PR | 5W-1 | 12.1417 | 528892 | 2.5 | 0.35714 | 15740.8333 | 117741.4333 | 1 | 0.14286 | 6296.3333 | 47096.5733 | 15 | 705 | 15 | 705 | 12.8586 |  | 352.5
| 5W-2 | 12.5659 | 547372 | 2.5 | 0.35714 | 16290.8333 | 121855.4333 | 1 | 0.14286 | 6516.3333 | 48742.1733 | 18 | 846 | 18 | 846 | 11.0899 |  | 423
| 5W-3 | 13.4787 | 587132 | 2.5 | 0.35714 | 17474.1667 | 130706.7667 | 1 | 0.14286 | 6989.6667 | 52282.7067 | 19 | 893 | 19 | 893 | 11.2694 |  | 446.5
PR | SPRAY 1 | 5.1096 | 222575 | 2.5 | 0.35714 | 6624.256 | 49549.4345 | 1 | 0.14286 | 2649.7024 | 19819.7738 |  | 850 |  | 850 | 4.4882 |  | 425
PR | SPRAY 2 | 17.101 | 744921 | 2.5 | 0.35714 | 22170.2679 | 165833.6036 | 1 | 0.14286 | 8868.1071 | 66333.4414 |  | 1200 |  | 1200 | 10.64 |  | 600
PR | SPRAY 3 | 8.3618 | 364240 | 2.5 | 0.35714 | 10840.4762 | 81086.7619 | 1 | 0.14286 | 4336.1905 | 32434.7048 | Given in/wk&mo | 1200 |  | 1200 | 5.2026 |  | 600
PR | SPRAY 4 | 6.3963 | 278623 | 2.5 | 0.35714 | 8292.3512 | 62026.7869 | 1 | 0.14286 | 3316.9405 | 24810.7148 | Capacity (avg gpd) | 1200 |  | 1200 | 3.9797 |  | 600
| TOTAL | 75.1551 |  |  |  | 97433.1845 | 728800.2202 |  |  | 38973.2738 | 291520.0881 | 400840.1211 | 6894 |  |  | 8.1393 | Given Hrs/wk - GPM | 3447
| GROSS | 157.7 | [10 empty] | GPM Hrs |  |  | 56112.6567 |  | 0.5
| % COVERAGE | 47.66% | [10 empty] | Given Hrs/wk |  |  | 1402.8164
| Spray Field 6 | [5 empty] | FIELD 6 (B)
GIVEN IN/WK
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY |  | GPM | Number heads | GPM | HOUR/WK
PR | 6W-1 | 12.6143 | 549479 | 2.5 | 0.35714 | 16353.5417 | 122324.4917 | 1 | 0.14286 | 6541.4167 | 48929.7967 | 19 | 893 | 19 | 893 | 10.5466 |  | 446.5
| 6W-2 | 13.564 | 590850 | 2.5 | 0.35714 | 17584.8214 | 131534.4643 | 1 | 0.14286 | 7033.9286 | 52613.7857 | 22 | 1034 | 22 | 1034 | 9.7943 |  | 517
| 6W-3 | 14.1727 | 617363 | 2.5 | 0.35714 | 18373.8988 | 137436.7631 | 1 | 0.14286 | 7349.5595 | 54974.7052 | 22 | 1034 | 22 | 1034 | 10.2337 |  | 517
| 6W-4 | 12.9046 | 562124 | 2.5 | 0.35714 | 16729.881 | 125139.5095 | 1 | 0.14286 | 6691.9524 | 50055.8038 | 21 | 987 | 21 | 987 | 9.7618 |  | 493.5
| 6W-5 | 11.1166 | 484240 | 2.5 | 0.35714 | 14411.9048 | 107801.0476 | 1 | 0.14286 | 5764.7619 | 43120.419 | 18 | 846 | 18 | 846 | 9.8108 |  | 423
| 6W-6 | 10.675 | 465003 | 2.5 | 0.35714 | 13839.375 | 103518.525 | 1 | 0.14286 | 5535.75 | 41407.41 | 17 | 799 | 17 | 799 | 9.9752 |  | 399.5
| 6W-7 | 11.2421 | 489707 | 2.5 | 0.35714 | 14574.6131 | 109018.106 | 1 | 0.14286 | 5829.8452 | 43607.2424 | 17 | 799 | 17 | 799 | 10.5052 |  | 399.5
EX | SPRAY 1 | 30.2629 | 1318250 | 2.5 | 0.35714 | 39233.631 | 293467.5595 | 1 | 0.14286 | 15693.4524 | 117387.0238 |  | 900 |  | 900 | 25.1056 |  | 900 | 826 | 0.5 | 1071715.7294 | 2594.9533 | 10.76 | 241.1667 | 4.0194 | 900 | 217050.0006 | 29017.3798 | 0.32491 | 0.080834
EX | SPRAY 2 | 107.8296 | 4697059 | 2.5 | 0.35714 | 139793.4226 | 1045654.8012 | 1 | 0.14286 | 55917.369 | 418261.9205 |  | 1050 |  | 1050 | 76.6746 |  | 1050 | 1108 | 1 | 3856816.9458 | 6961.7634 | 10.76 | 647.004 | 10.7834 | 1050 | 679354.239 | 90822.7592 | 0.28258 | 0.026205
PR | SPRAY 3 | 9.337 | 406719 | 2.5 | 0.35714 | 12104.7321 | 90543.3964 | 1 | 0.14286 | 4841.8929 | 36217.3586 |  | 850 |  | 850 | 8.2014 |  | 425
PR | SPRAY 4 | 27.6703 | 1205318 | 2.5 | 0.35714 | 35872.5595 | 268326.7452 | 1 | 0.14286 | 14349.0238 | 107330.6981 | Given in/wk&mo | 1200 |  | 1200 | 17.2161 |  | 600
PR | SPRAY 5 | 38.983 | 1698099 | 2.5 | 0.35714 | 50538.6607 | 378029.1821 | 1 | 0.14286 | 20215.4643 | 151211.6729 | Capacity (avg gpd) | 1200 |  | 1200 | 24.2547 |  | 1200
| TOTAL | 300.3722 |  |  |  | 389411.0417 | 2912794.5917 |  |  | 155764.4167 | 1165117.8367 | 1602037.0254 | 11592 |  |  | 19.3466 | Given Hrs/wk - GPM | 7371
| GROSS | 395.1 | [10 empty] | GPM Hrs |  |  | 224265.359 |  | 0.63587
| % COVERAGE | 76.02% | [10 empty] | Given Hrs/wk |  |  | 5606.634
| Spray Field 7 | [5 empty] | FIELD 7 (A)
GIVEN IN/WK
| SUB AREA | AREA | AREA | MAX APPLICATION RATE |  | MAX QUANITY OF WATER APPLIED |  | ACTUAL APPLICATION RATE |  | ACTUAL QUANTITY APPLIED |  |  | FLOW |  | FLOW | RUN TIME MAX
|  | ACRES | SQFT | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY | IN/WEEK | IN/DAY | CF/DAY | GAL/DAY |  | GPM | Number heads | GPM | HOUR/WK
PR | 7W-1 | 16.0058 | 697213 | 2.5 | 0.35714 | 20750.3869 | 155212.894 | 1 | 0.14286 | 8300.1548 | 62085.1576 | 24 | 1128 | 24 | 1128 | 10.5943 |  | 564
| 7W-2 | 18.0707 | 787158 | 2.5 | 0.35714 | 23427.3214 | 175236.3643 | 1 | 0.14286 | 9370.9286 | 70094.5457 | 29 | 1363 | 29 | 1363 | 9.8988 |  | 681.5
PR | SPRAY 1 | 18.6927 | 814256 | 2.5 | 0.35714 | 24233.8095 | 181268.8952 | 1 | 0.14286 | 9693.5238 | 72507.5581 |  | 1200 |  | 1200 | 11.6304 |  | 600
PR | SPRAY 2 | 7.1786 | 312698 | 2.5 | 0.35714 | 9306.4881 | 69612.531 | 1 | 0.14286 | 3722.5952 | 27845.0124 |  | 1200 |  | 1200 | 4.4664 |  | 600
PR | SPRAY 3 | 9.8325 | 428302 | 2.5 | 0.35714 | 12747.0833 | 95348.1833 | 1 | 0.14286 | 5098.8333 | 38139.2733 |  | 1200 |  | 1200 | 6.1176 |  | 600
PR | SPRAY 4 | 7.838 | 341424 | 2.5 | 0.35714 | 10161.4286 | 76007.4857 | 1 | 0.14286 | 4064.5714 | 30402.9943 |  | 1200 |  | 1200 | 4.8767 |  | 600
PR | SPRAY 5 | 45.7842 | 1994358 | 2.5 | 0.35714 | 59355.8929 | 443982.0786 | 1 | 0.14286 | 23742.3571 | 177592.8314 |  | 1200 |  | 1200 | 28.4863 |  | 1200
PR | SPRAY 6 | 12.9428 | 563787 | 2.5 | 0.35714 | 16779.375 | 125509.725 | 1 | 0.14286 | 6711.75 | 50203.89 | Given in/wk&mo | 1200 |  | 1200 | 8.0528 |  | 600
PR | SPRAY 7 | 14.067 | 612757 | 2.5 | 0.35714 | 18236.8155 | 136411.3798 | 1 | 0.14286 | 7294.7262 | 54564.5519 | Capacity (avg gpd) | 1200 |  | 1200 | 8.7523 |  | 600
| TOTAL | 150.4121 |  |  |  | 194998.6012 | 1458589.5369 |  |  | 77999.4405 | 583435.8148 | 802224.2453 | 10891 |  |  | 10.3114 | Given Hrs/wk - GPM | 6045.5
| GROSS | 181.8 | [10 empty] | GPM Hrs |  |  | 112301.4671 |  | 0.55509
| % COVERAGE | 82.73% | [10 empty] | Given Hrs/wk |  |  | 2807.5367
| TOTAL (ALL FIELDS) |  | 1326.4969 | ACRES
| GROSS (ALL FIELDS) |  | 1721.4 | ACRES |  |  |  | SPRAY FIELD | TOTAL FLOW
| % COVERAGE |  | 77.06% |  |  |  |  | 1 | 19044 | 1
[8 empty] | 2 | 3900 | 0.37143
[8 empty] | 3 | 3302 | 0.31448
| existing equip | 491.2255 | [5 empty] | 4 | 5959 | 0.56752
| proposed field | 418.4819 | [5 empty] | 5 | 6894 | 0.65657
| proposed woods | 416.7895 | 835.2714 |  |  |  |  | 6 | 11592 | 1
[8 empty] | 7 | 10891 | 1
[8 empty] | TOTAL | 61582
118
|  |  |  | 137 |  |  |  | PUMP STATION FLOW RATE | 10500
|  |  |  | 156 | 4
175
194
14
685
13
|  |  |  | 23 | 0
|  |  |  | 32 | 1
42
51
61
SOLID SETS
OPTIONS
| DIA (FT) | FLOW (GPM) | AREA (SQ FT) | IN/HR
| 200 | 100 | 31415.9 | 0.30639
| 191 | 47 | 28652.0862 | 0.1579 | USE
| 262 | 152 | 53912.826 | 0.27138

## South
TOTAL DYNAMIC HEAD LOSS CALCULATIONS |  |  |  |  | STARTING ELEV: | 21
[5 empty] | HEIGHT OF IRRIGATION EQUIP: | 10
[5 empty] | HIGH SITE ELEV | 45
|  | MINIMUM OPERATING POINT |  |  | STATIC HEAD: | 34
|  | 11922 | = DESIGN FLOW (GPM) |  | FRICTION HEAD: | 94.2675
|  | 94.2675 | = TDH AT DESIGN FLOW |  | TDH: | 128.2675
SYSTEM CURVE
|  | 0 | = STARTING FLOW (GPM)
|  | 20 | = FLOW STEP (GPM)
RUN |  | SECTION | SECTION
|  | 1 | 2
DIA. |  | 24 | 24
EQ. FT. |  | 240 | 11100
"C" |  | 110 | 110
FLOW |  | 24759.8929 | 9415.9979
|  | DYN. HD. | DYN. HD. | TOTAL
|  | 10.8133 | 83.4542 | 94.2675
SUMMARY
LENGTH | L/D | 120 | 11000
90'S | 30 | 0 | 1
45'S | 14
T RUN | 20 | 0
T BRANCH | 60 | 1
VALVE | 18
CHK VALVE | 50
REDUCER | 20 | 0 | 1
EQ. LENGTH
LENGTH |  | 120 | 11000
90'S |  | 0 | 60
45'S |  | 0 | 0
T RUN |  | 0 | 0
T BRANCH |  | 120 | 0
VALVE |  | 0 | 0
CHK VALVE |  | 0 | 0
REDUCER |  | 0 | 40
TOTAL |  | 240 | 11100

## North
TOTAL DYNAMIC HEAD LOSS CALCULATIONS | [5 empty] | STARTING ELEV: | 21
[6 empty] | HEIGHT OF IRRIGATION EQUIP: | 10
[6 empty] | HIGH SITE ELEV | 34
|  | MINIMUM OPERATING POINT |  |  |  | STATIC HEAD: | 23
|  | 6046 | = DESIGN FLOW (GPM) |  |  | FRICTION HEAD: | 175.6358
|  | 175.6358 | = TDH AT DESIGN FLOW |  |  | TDH: | 198.6358
SYSTEM CURVE
|  | 0 | = STARTING FLOW (GPM)
|  | 20 | = FLOW STEP (GPM)
RUN |  | SECTION | SECTION | SECTION | SECTION
|  | 1 | 3 | 8 | 9
DIA. |  | 24 | 24 | 24 | 16
EQ. FT. |  | 240 | 4440 | 11416 | 2200
"C" |  | 110 | 110 | 110 | 110
FLOW |  | 24759.8929 | 15343.8949 | 8414.1707 | 2807.5367
|  | DYN. HD. | DYN. HD. | DYN. HD. | DYN. HD. | TOTAL
|  | 10.8133 | 82.4633 | 69.6883 | 12.671 | 175.6358
SUMMARY
LENGTH | L/D | 120 | 4400 | 11300 | 2200
90'S | 30 | 0 | 0 | 1
45'S | 14 |  | 0 | 2
T RUN | 20 | 0
T BRANCH | 60 | 1
VALVE | 18
CHK VALVE | 50
REDUCER | 20 | 0 | 1
EQ. LENGTH
LENGTH |  | 120 | 4400 | 11300 | 2200
90'S |  | 0 | 0 | 60 | 0
45'S |  | 0 | 0 | 56 | 0
T RUN |  | 0 | 0 | 0 | 0
T BRANCH |  | 120 | 0 | 0 | 0
VALVE |  | 0 | 0 | 0 | 0
CHK VALVE |  | 0 | 0 | 0 | 0
REDUCER |  | 0 | 40 | 0 | 0
TOTAL |  | 240 | 4440 | 11416 | 2200

## West
TOTAL DYNAMIC HEAD LOSS CALCULATIONS | [5 empty] | STARTING ELEV: | 21
[6 empty] | HEIGHT OF IRRIGATION EQUIP: | 10
[6 empty] | HIGH SITE ELEV | 38
|  | MINIMUM OPERATING POINT |  |  |  | STATIC HEAD: | 27
|  | 2076 | = DESIGN FLOW (GPM) |  |  | FRICTION HEAD: | 129.1724
|  | 129.1724 | = TDH AT DESIGN FLOW |  |  | TDH: | 156.1724
SYSTEM CURVE
|  | 0 | = STARTING FLOW (GPM)
|  | 20 | = FLOW STEP (GPM)
RUN |  | SECTION | SECTION | SECTION
|  | 1 | 3 | 7
DIA. |  | 24 | 24 | 10
EQ. FT. |  | 240 | 4440 | 1250
"C" |  | 110 | 110 | 110
FLOW |  | 24759.8929 | 15343.8949 | 1942.3451
|  | DYN. HD. | DYN. HD. | DYN. HD. | TOTAL
|  | 10.8133 | 82.4633 | 35.8958 | 129.1724
SUMMARY
LENGTH | L/D | 120 | 4400 | 1200
90'S | 30 | 0 | 0
45'S | 14 |  | 0
T RUN | 20 | 0 |  | 0
T BRANCH | 60 | 1 |  | 1
VALVE | 18
CHK VALVE | 50
REDUCER | 20 | 0 | 1
EQ. LENGTH
LENGTH |  | 120 | 4400 | 1200
90'S |  | 0 | 0 | 0
45'S |  | 0 | 0 | 0
T RUN |  | 0 | 0 | 0
T BRANCH |  | 120 | 0 | 50
VALVE |  | 0 | 0 | 0
CHK VALVE |  | 0 | 0 | 0
REDUCER |  | 0 | 40 | 0
TOTAL |  | 240 | 4440 | 1250

## East
TOTAL DYNAMIC HEAD LOSS CALCULATIONS | [5 empty] | STARTING ELEV: |  | 21
[6 empty] | HEIGHT OF IRRIGATION EQUIP: |  | 10
[6 empty] | HIGH SITE ELEV |  | 24
|  | MINIMUM OPERATING POINT |  |  |  | STATIC HEAD: |  | 13
|  | 3447 | = DESIGN FLOW (GPM) |  |  | FRICTION HEAD: |  | 182.0027
|  | 182.0027 | = TDH AT DESIGN FLOW |  |  | TDH: |  | 195.0027
SYSTEM CURVE
|  | 0 | = STARTING FLOW (GPM)
|  | 20 | = FLOW STEP (GPM)
RUN |  | SECTION | SECTION | SECTION | SECTION | SECTION
|  | 1 | 3 | 4 | 5 | 6
DIA. |  | 24 | 24 | 16 | 14 | 12
EQ. FT. |  | 240 | 4440 | 1906.6667 | 1893.3333 | 4380
"C" |  | 110 | 110 | 110 | 111 | 110
FLOW |  | 24759.8929 | 15343.8949 | 4987.3792 | 3354.2162 | 1402.8164
|  | DYN. HD. | DYN. HD. | DYN. HD. | DYN. HD. | DYN. HD. | TOTAL
|  | 10.8133 | 82.4633 | 31.829 | 28.5662 | 28.3309 | 182.0027
SUMMARY
LENGTH | L/D | 120 | 4400 | 1800 | 1800 | 4300
90'S | 30 | 0 | 0 |  |  | 2
45'S | 14 |  | 0
T RUN | 20 | 0 |  | 0 | 0
T BRANCH | 60 | 1 |  | 1 | 1
VALVE | 18
CHK VALVE | 50
REDUCER | 20 | 0 | 1 | 1 | 1 | 1
EQ. LENGTH
LENGTH |  | 120 | 4400 | 1800 | 1800 | 4300
90'S |  | 0 | 0 | 0 | 0 | 60
45'S |  | 0 | 0 | 0 | 0 | 0
T RUN |  | 0 | 0 | 0 | 0 | 0
T BRANCH |  | 120 | 0 | 80 | 70 | 0
VALVE |  | 0 | 0 | 0 | 0 | 0
CHK VALVE |  | 0 | 0 | 0 | 0 | 0
REDUCER |  | 0 | 40 | 26.6667 | 23.3333 | 20
TOTAL |  | 240 | 4440 | 1906.6667 | 1893.3333 | 4380